## Division 23 Checklist
Division 23 HVAC Closeout Checklist
closeoutdesk.com ¦ Track your Division 23 submission completeness ¦ Mark N/A for items not applicable to this project
# | Document / Requirement | Category | Blocks CO? | Status | Responsible Party | Date Due | Date Received | Notes
1 | TAB report from NEBB- or AABC-certified agency (not the mechanical contractor) | TAB Report | Y
2 | TAB report covers all air terminal units — 100% terminal coverage, no rooms omitted | TAB Report | Y
3 | TAB report covers all hydronic circuits (coils, pumps, heat exchangers) | TAB Report | Y
4 | AHU total supply airflows within +/- 10% of design values | TAB Report | Y
5 | TAB agency certification page signed by TAB engineer of record | TAB Report | Y
6 | Exhaust airflow verification — all exhaust systems measured and within design tolerance (bathroom, kitchen, lab, general exhaust) | TAB Report | N
7 | ATC/BAS sequences of operation — as-built version signed by controls contractor | Controls / BAS | N
8 | BAS point-to-point checkout documentation | Controls / BAS | N
9 | BAS graphics and display documentation — as-programmed screen layouts for all zones and equipment | Controls / BAS | N
10 | BAS/controls owner training — signed attendance sheet confirming owner's facilities staff were trained | Controls / BAS | N
11 | O&M manuals: Air handling units — model-specific for each installed unit | O&M Manuals | N
12 | O&M manuals: Rooftop units — model-specific for each installed unit | O&M Manuals | N
13 | O&M manuals: Fan coil units — by model | O&M Manuals | N
14 | O&M manuals: Energy recovery ventilators | O&M Manuals | N
15 | O&M manuals: Chillers (mark N/A if not on project) | O&M Manuals | N
16 | O&M manuals: Boilers and domestic water heaters (mark N/A if not on project) | O&M Manuals | N
17 | O&M manuals: Cooling towers (mark N/A if not on project) | O&M Manuals | N
18 | O&M manuals: VRF/VRV systems including zone controller documentation (mark N/A if not on project) | O&M Manuals | N
19 | O&M manuals: All other HVAC equipment not listed above | O&M Manuals | N
20 | Approved equipment submittals confirming installed products, models, and specifications | O&M Manuals | N
21 | Manufacturer startup reports for all major equipment | Startup / Commissioning | Y
22 | Factory startup certificate for all equipment requiring manufacturer startup | Startup / Commissioning | Y
23 | Commissioning report (if Cx is in scope — mark N/A otherwise) | Startup / Commissioning | N
24 | Functional performance test records (if Cx is in scope) | Startup / Commissioning | N
25 | Commissioning issues log with resolution status for all deficiencies | Startup / Commissioning | N
26 | Cx agent sign-off letter confirming final acceptance (if Cx is in scope) | Startup / Commissioning | N
27 | Warranty letters/certificates for all major HVAC equipment — one per piece of equipment | Warranties | N
28 | Extended warranty certificates where required by specification (compressor, heat exchanger, etc.) | Warranties | N
29 | Warranty registration confirmation for all equipment requiring manufacturer registration within 30–60 days of startup | Warranties | N
30 | Refrigerant tracking log — refrigerant type and initial charge weight per system | Refrigerant | N
31 | EPA Section 608 technician certification confirmation | Refrigerant | N
32 | As-built mechanical drawings reflecting all field changes from design documents | As-Builts & Field Records | N
33 | Equipment schedule reflecting installed products with model numbers and serial numbers | As-Builts & Field Records | N
34 | Duct leakage test report (if required by specification) | As-Builts & Field Records | N
35 | Hydronic pipe pressure test records — chilled water, hot water, and condenser water piping loops | As-Builts & Field Records | N
36 | Chemical water treatment startup report from certified water treatment contractor confirming initial charge | Water Treatment | N
37 | Ongoing water treatment program documentation, product data sheets, and service contact information | Water Treatment | N
38 | Spare parts and consumables delivery confirmation — filters, belts, bearings, and other items required by specification | Spare Parts & Attic Stock | N
39 | Attic stock delivery receipt signed by owner's representative confirming receipt of spare materials | Spare Parts & Attic Stock | N
Status color key: ✅ Accepted (green) ⏳ Submitted (yellow) 🚫 Blocked (red) — N/A (gray) □ Pending (blank)
Blocks CO? Y = item is typically required before the Certificate of Occupancy can be issued. N = important but not a CO condition.